LXLC(R)-40~65(mm)

Removable element woltman cold (hot) water meter

Application:

--Measuring the total volume of cold(hot) water passing through the pipeline.

-NOTE:This type of water meter can be used for a reading transmission system as equipped with pluse.

Feature:

-- Dry-dial, Magnetic drive

----Vacuum sealed register ensures the dial keep free from fog and Keep the reading clear in a long term service;

--Removable element unit and strong universality, easy installation and maintenance,

--Measuing high flow rate with low head loss.

-- Remote transmission device can be added upon request,such as Reed Swith or Hall, Pulse Output:DN40-65mm 1000L/P、100L/P.

--Technical data conform to international standard ISO 4064..

Working condition

Water temperature: T30 T50 T90

Water pressure class: MAP16  MAP10

Pressure-loss Class: △p63

Maximum permissible errors

(1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%.

(2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%;

(Hot water meter ±3%)

### MAIN TECHNICAL SPECIFICATIONS

| Type | Size | Class | Q4 Overload Flow | Q3 Permanent Flow | Q2 Transitional Flow | Q1 Min. Flow | Min. Reading | Max. Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | m3/h |  |  |  | m3 |  |
| LXLC-40 | 1½" | R50 (R80) | 31.25 | 25 | 0.8 | 0.5 | 0.0005 | 999,999 |
| LXLC-50 | 2" |  | 31.25 | 25 | 0.8 | 0.5 | 0.0005 | 999,999 |
| LXLC-65 | 2½" |  | 50 | 40 | 1.28 | 0.8 | 0.0005 | 999,999 |

### DIMENSIONS

| Type | Size |  | L Length |  | H Height | Connecting flange |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | φD1 Outside diameter | φD2 Bolt circle diameter | Connecting Bolts (n-M) |
|  | mm |  |  |  |  |  |  |  |
| LXLC-40 | 1½" | 200 |  | 210 |  | 150 | 110 | 4-M16 |
| LXLC-50 | 2" | 200 |  | 214 |  | 165 | 125 | 4-M16 |
| LXLC-65 | 2½" | 200 |  | 224 |  | 185 | 145 | 4-M16 |

NOTE: The flange dimension conforms to ISO7005-2:1988 standard. Order for products of special requirements is also accepted.

| LXLC-40～65 REMOVABLE ELEMENT WOLTMAN WATER METER |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Screw For Sealing | Stainless Steel | 1 |
| 2 | Cover With Lid | Assembly | 1 |
| 3 | Sealed Register | Assembly | 1 |
| 4 | Screw M4×20 | Stainless Steel | 2 |
| 5 | Flange Plate | Cast Iron | 2 |
| 6 | O-ring | Silicon Rubber | 1 |
| 7 | Screw | Stainless Steel | 1 |
| 8 | Adjusting Lever | POM OR MPPO | 1 |
| 9 | Adjusting Plate | POM OR MPPO | 1 |
| 10 | Turbine | ABS OR MPPO | 1 |
| 11 | Rectifier | ABS OR MPPO | 1 |
| 12 | Body | Casting Iron | 1 |
| 13 | Screw | Stainless Steel | 1 |
| 14 | Screw | Stainless Steel | 1 |
| 15 | Fixed plate | POM OR MPPO | 1 |
| 16 | Screw | Stainless Steel | 1 |
| 17 | Gasket | Stainless Steel | 1 |
| 18 | Upper Bearing Plate | Brass | 1 |
| 19 | Upper Bearing | Nylon With Graphite | 1 |
| 20 | Magnet Component | Component | 1 |
| 21 | Lower Bearing | Nylon With Graphite | 1 |
| 22 | Screw | Stainless Steel | 1 |
| 23 | Support | POM OR MPPO | 1 |
| 24 | Seal Gasket | Rubber | 1 |

----------------------------------------------------------------------------------------------------------------------

LIANYUNGANG HYTTEN METER CO.,LTD.

Add:No. 8 Hanguo Industrial Development Zone,Luoyang Village

Dunshang Town,Ganyu District, Lianyungang, Jiangsu, China

Tel:      ++86-518-85907891

Fax:     ++86-518-85907890             Postal code:   222000

E-mail: hytten@hyttenmeter.com

http://www.hyttenmeter.com    www.hyttenwatermeter.com