LXLC(R)-80~200(mm)

Removable element woltman cold (hot) water meter

Application:

--Measuring the total volume of cold(hot) water passing through the pipeline.

-NOTE:This type of water meter can be used for a reading transmission system as equipped with pluse.

Feature:

-- Dry-dial, Magnetic drive

----Vacuum sealed register ensures the dial keep free from fog and Keep the reading clear in a long term service;

--Removable element unit and strong universality, easy installation and maintenance,

--Measuing high flow rate with low head loss.

-- Remote transmission device can be added upon request,such as Reed Swith or Hall, Pulse Output:DN80-200mm 1000L/P、100L/P.

--Technical data conform to international standard ISO 4064..

Working condition

Water temperature: T30 T50 T90

Water pressure class: MAP16  MAP10

Pressure-loss Class: △p63

Maximum permissible errors

(1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%.

(2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%;

(Hot water meter ±3%)

### MAIN TECHNICAL SPECIFICATIONS

| Type | Size | Class | Q4 Overload Flow | Q3 Permanent Flow | Q2 Transitional Flow | Q1 Min. Flow | Min. Reading | Max. Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | m3/h |  |  |  | m3 |  |
| LXLC-80 | 3" | R50 (R80) | 78.75 | 63 | 2 | 1.26 | 0.002 | 999,999 |
| LXLC-100 | 4" |  | 125 | 100 | 3.2 | 2 | 0.002 | 999,999 |
| LXLC-125 | 5" |  | 200 | 160 | 5.12 | 3.2 | 0.002 | 999,999 |
| LXLC-150 | 6" |  | 312.5 | 250 | 8 | 5 | 0.002 | 999,999 |
| LXLC-200 | 8" |  | 500 | 400 | 12.8 | 8 | 0.002 | 999,999 |

### DIMENSIONS

| Type | Size |  | L Length |  | H Height | Connecting flange |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | φD1 Outside diameter | φD2 Bolt circle diameter | Connecting Bolts (n-M) |
|  | mm |  |  |  |  |  |  |  |
| LXLC-80 | 3" | 225 |  | 279 |  | 200 | 160 | 8-M16 |
| LXLC-100 | 4" | 250 |  | 289 |  | 220 | 180 | 8-M16 |
| LXLC-125 | 5" | 250 |  | 299 |  | 250 | 210 | 8-M16 |
| LXLC-150 | 6" | 300 |  | 319 |  | 285 | 240 | 8-M20 |
| LXLC-200 | 8" | 350 |  | 346 |  | 340 | 295 | 8-M20(1.0MPa) |
|  |  |  |  |  |  |  |  | 12-M20(1.6MPa) |

NOTE: The flange dimension conforms to ISO7005-2:1988 standard. Order for products of special requirements is also accepted.

| LXLC-80～200 REMOVABLE ELEMENT WOLTMAN WATER METER |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Screw For Sealing | Stainless Steel | 1 |
| 2 | Cover With Lid | Assembly | 1 |
| 3 | Sealed Register | Assembly | 1 |
| 4 | Screw M4×20 | Stainless Steel | 2 |
| 5 | Gasket | Brass | 2 |
| 6 | Adjusting Nut | Brass | 1 |
| 7 | Flange Cover | Cast Iron | 1 |
| 8 | O-ring | Silicon Rubber | 1 |
| 9 | Bush | Brass | 1 |
| 10 | Gasket | Synthetic Rubber | 1 |
| 11 | Adjusting Lever | Brass | 1 |
| 12 | Connecting Lever | POM OR MPPO | 1 |
| 13 | Adjusting Plate | POM OR MPPO | 1 |
| 14 | Support | ABS OR MPPO | 1 |
| 15 | Turbine Component | Assembly | 1 |
| 16 | Rectifier | ABS OR MPPO | 1 |
| 17 | Screw | Brass | 1 |
| 18 | O-ring | Synthetic Rubber | 1 |
| 19 | Body | Cast Iron | 1 |
| 20 | Screw For Sealing | Stainless Steel | 1 |
| 21 | Screw For Sealing | Stainless Steel | 3 |
| 22 | Support | ABS | 1 |
| 23 | Screw M4×20 | Stainless Steel | 2 |
| 24 | Gasket | Stainless Steel | 4 |
| 25 | Upper Bearing Plate | Brass | 1 |
| 26 | Upper Bearing | Nylon With Graphite | 1 |
| 27 | Magnet Component | Component | 1 |
| 28 | Transmission Shaft | Stainless Steel | 1 |
| 29 | Sheath | Nylon | 2 |
| 30 | Bevel Gear | POM | 1 |
| 31 | Bevel Gear | Nylon | 1 |
| 32 | Gasket | Stainless Steel | 4 |
| 33 | ScrewM5X12 | Stainless Steel | 4 |
| 34 | Nut | Brass | 1 |
| 35 | Gasket | Brass | 1 |
| 36 | Turbine Shaft Hold | Brass | 1 |
| 37 | Turbine Shaft | Tungsten Steel | 1 |

----------------------------------------------------------------------------------------------------------------------

LIANYUNGANG HYTTEN METER CO.,LTD.

Add:No. 8 Hanguo Industrial Development Zone,Luoyang Village

Dunshang Town,Ganyu District, Lianyungang, Jiangsu, China

Tel:      ++86-518-85907891

Fax:     ++86-518-85907890             Postal code:   222000

E-mail: hytten@hyttenmeter.com

http://www.hyttenmeter.com    www.hyttenwatermeter.com