Ws 40-200mm

Woltman Vertical Installation type Dry-dial water meter

Application:

--Measuring the total volume of cold water passing through the pipeline.

Note: It is a Vertical Woltman water meter for industril and Irrigation application in sizes from 50 to 200mm for cold meter.
Features
--Removable measruing unit,Inner filter,easy manintance.

-- Dry dial register, Magnetic drive,keep clear reading for long time.
-- Low start flow, low pressure loss at high flowrate, better than vane wheel meter.

--Can make Photoelectric direct reading remote transmission and OUTPUT water meter,Remote transmission device can be added upon request,such as Reed Switch or Hall, Pulse Output:1000L/P、100L/P.

--Technical data conform to international standard ISO 4064.

Working condition

Water temperature: T30 T50 T90

Water pressure class: MAP16  MAP10

Pressure-loss Class: △p63

Accuracy:

(1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%.

(2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%;

(Hot water meter ±3%)

- MAIN TECHNICAL SPECIFICATIONS

| TYPE | Size mm | Permanent flow Q4 | Overload Flow Q3 | Q3/Q1 | Q2/Q1 | Transmission Flow Q2 | Min Flow Q1 | Min Reading | Max Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (m3/h) |  |  |  | m3 |  |  |  |
| WS-40 | 1½" | 50 | 40 | 160 | 1.6 | 0.4 | 0.25 | 0.0005 | 999,999 |
|  |  |  |  |  | 6.3 | 1.58 |  |  |  |
| WS-50 | 2" | 50 | 40 | 160 | 1.6 | 0.4 | 0.25 |  |  |
|  |  |  |  |  | 6.3 | 1.58 |  |  |  |
|  |  |  |  | 200 | 1.6 | 0.32 | 0. 2 |  |  |
|  |  |  |  |  | 6.3 | 1.26 |  |  |  |
| WS-65 | 2½" | 50 | 40 | 160 | 1.6 | 0.4 | 0.25 |  |  |
|  |  |  |  |  | 6.3 | 1.58 |  |  |  |
|  |  |  |  | 200 | 1.6 | 0. 32 | 0.2 |  |  |
|  |  |  |  |  | 6.3 | 1.26 |  |  |  |
| WS-80 | 3" | 79 | 63 | 160 | 1.6 | 0. 63 | 0. 39 |  |  |
|  |  |  |  |  | 6.3 | 2.48 |  |  |  |
|  |  |  |  | 200 | 1.6 | 0.5 | 0. 32 |  |  |
|  |  |  |  |  | 6.3 | 2 |  |  |  |
| WS-100 | 4" | 125 | 100 | 160 | 1.6 | 1 | 0. 63 |  |  |
|  |  |  |  |  | 6.3 | 3.94 |  |  |  |
|  |  |  |  | 200 | 1.6 | 0.8 | 0.5 |  |  |
|  |  |  |  |  | 6.3 | 3. 15 |  |  |  |
| WS-150 | 5" | 312 | 250 | 160 | 1.6 | 2.5 | 1.56 |  |  |
|  |  |  |  |  | 6.3 | 9.8 |  |  |  |
|  |  |  |  | 200 | 1.6 | 2 | 1.25 |  |  |
|  |  |  |  |  | 6.3 | 7.9 |  |  |  |
| WS-200 | 6" | 500 | 400 | 160 | 1.6 | 4 | 2.5 |  |  |
|  |  |  |  |  | 6.3 | 15.8 |  |  |  |
|  |  |  |  | 200 | 1.6 | 3.2 | 2 |  |  |
|  |  |  |  |  | 6.3 | 12.6 |  |  |  |

DIMENSION

| Type DN (mm) | Length L (mm) | Height H (mm) | CONNECTING flange |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Outside Diameter D | Bolt circle diameter D1 (mn) | Connecting Bolts (n-M) |
| WS-40 | 245 | 280 | -- | -- | R1½"(螺纹连接） |
| WS-50 | 280 | 280 | 165 | 125 | 4XM16 |
| WS-65 | 280 | 280 | 185 | 145 | 4XM16 |
| WS-80 | 370 | 300 | 200 | 160 | 8XM16 |
| WS-100 | 370 | 305 | 220 | 180 | 8XM16 |
| WS-150 | 500 | 500 | 285 | 240 | 8XM20 |
| WS-200 | 500 | 515 | 340 | 295 | 8XM20 |

| WS-40～200 Woltman Vertical InstallationType Dry-Dial Water Meter |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Cover with lid | Assembly | 1 |
| 2 | Sealed Register | Assembly | 1 |
| 3 | Screw | Stainless Steel | 1 |
| 4 | Mechanism | Assembly | 1 |
| 5 | Body | Grey cast iron | 1 |
| 6 | Screw | Stainless Steel | 2 |
| 7 | Screw | Stainless Steel | 1 |
| 8 | O-ring | Rubber | 1 |
| 9 | O-ring | Rubber | 1 |

LIANYUNGANG HYTTEN METER CO.,LTD.

Address: NO.8 Hanguo Industrial Development Zone,Luoyang village,Dunshang Town,Ganyu District, Lianyungang City.

Tel：0518-85907891         Fax：0518-85907892

Http：//www. hyttenmeter.com  E-mail：hytten@hyttenmeter.com