LXLC-50-300/ZD

Photoelectric direct reading Water Meter

Application:

--Measuring the total volume of cold(hot) water passing through the pipeline.

-NOTE:This type of water meter can be used for a reading transmission system as equipped with a built-in-sensor

Feature:

--Reading data directly, realizes“zero”error basiclly

--Low power design.

--The intelligent electronic unit is completely sealed in the register to effectively avoid the erosion of external water and moisture.

--Meet electromagnetic compatibility design requirement for EMC,ESD,EMI etc electronic products.

--The fault diagnosis shutdown technology is used to guarantee the safety of the whole network.

--Provide M-BUS transmission.

Working condition:

Water temperature: T30 T50 T90

Water pressure class: MAP16  MAP10

Pressure-loss Class: △p63

Installation environment: Class B

Electromagnetic environment: Class E1

Accurancy:

(1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%.

(2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%;

- Technical parameters

| 序号 | Communication mode | RS-485 | MBUS |
| --- | --- | --- | --- |
| 1 | working voltage | 9V～15V | 24V～42V |
| 2 | static current | ≤1mA | ≤2mA |
| 3 | wording current | ≤5mA | ≤10mA |
| 4 | Communication protocol | DL/T645、CJ/T 188（or customer requirements） |  |
| 5 | Communication rate | 1200/2400Baud |  |

- MAIN TECHNICAL SPECIFICATIONS(R50/80) LXLC

| Type | Size | Class | Overload Flow | Permanent Flow | Transitional Flow | Qmin Min. Flow | Min. Reading | Max. Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | m3/h |  |  |  | m3 |  |
| LXLC-50/ZD | 2" | R50 (R80) | 31.25 | 25 | 0.8 | 0.5 | 0.0005 | 999,999 |
| LXLC-65/ZD | 2½" |  | 50 | 40 | 1.28 | 0.8 | 0.0005 | 999,999 |
| LXLC-80/ZD | 3" |  | 78.75 | 63 | 2 | 1.26 | 0.002 | 999,999 |
| LXLC-100/ZD | 4" |  | 125 | 100 | 3.2 | 2 | 0.002 | 999,999 |
| LXLC-125/ZD | 5" |  | 200 | 160 | 5.12 | 3.2 | 0.002 | 999,999 |
| LXLC-150/ZD | 6" |  | 312.5 | 250 | 8 | 5 | 0.002 | 999,999 |
| LXLC-200/ZD | 8" |  | 500 | 400 | 12.8 | 8 | 0.002 | 999,999 |
| LXLC-250/ZD | 10" |  | 787.5 | 630 | 20.16 | 12.6 | 0.02 | 999,999 |
| LXLC-300/ZD | 12" |  | 1250 | 1000 | 32 | 20 | 0.02 | 9,999,999 |

- MAIN TECHNICAL SPECIFICATIONS(R20/25)  WI

| Type | Size | Class | Overload Flow | Permanent Flow | Transitional Flow | Qmin Min. Flow | Min. Reading | Max. Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | m3/h |  |  |  | m3 |  |
| LXXG-50/ZD | 2" | R20 (R25) | 31.25 | 25 | 5 | 1.25 | 0. 002 | 999,999 |
| LXXG-65/ZD | 2½" |  | 50 | 40 | 8 | 2 | 0.002 | 999,999 |
| LXXG-80/ZD | 3" |  | 78.75 | 63 | 12.6 | 3.15 | 0.002 | 999,999 |
| LXXG-100/ZD | 4" |  | 125 | 100 | 20 | 5 | 0.002 | 999,999 |
| LXXG-125/ZD | 5" |  | 200 | 160 | 32 | 8 | 0.002 | 999,999 |
| LXXG-150/ZD | 6" |  | 312.5 | 250 | 50 | 12.5 | 0.002 | 999,999 |
| LXXG-200/ZD | 8" |  | 500 | 400 | 80 | 20 | 0.002 | 999,999 |
| LXXG-250/ZD | 10" |  | 787.5 | 630 | 126 | 31.5 | 0.02 | 999,999 |
| LXXG-300/ZD | 12" |  | 1250 | 1000 | 200 | 50 | 0.02 | 9,999,999 |

- Dimensions

- Installation Requirement

- The meter should be installed in horizontal position with the direction of the flow as in dicated by the arrow cast in the meter body with the register face upwards;

- Pipeline must be flushed before installation;

- The meter should be constantly full of water during operation;

- The meter must have 10 diameters straight pipe ahead of the meter and 5 diameters straight pipe after to insure proper flow through the meter.

DIMENSION   LXLC

| Type | Size |  | L Length |  | H Height | Connecting flange |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | φD1 Outside diameter | φD2 Bolt circle diameter | Connecting Bolts (n-M) |
|  | mm |  |  |  |  |  |  |  |
| LXLC-50/ZD | 2" | 200 |  | 214 |  | 165 | 125 | 4-M16 |
| LXLC-65/ZD | 2½" | 200 |  | 224 |  | 185 | 145 | 4-M16 |
| LXLC-80/ZD | 3" | 225 |  | 279 |  | 200 | 160 | 8-M16 |
| LXLC-100/ZD | 4" | 250 |  | 289 |  | 220 | 180 | 8-M16 |
| LXLC-125/ZD | 5" | 250 |  | 299 |  | 250 | 210 | 8-M16 |
| LXLC-150/ZD | 6" | 300 |  | 319 |  | 285 | 240 | 8-M20 |
| LXLC-200/ZD | 8" | 350 |  | 346 |  | 340 | 295 | 8-M20(1.0MPa) |
|  |  |  |  |  |  |  |  | 12-M20(1.6MPa) |
| LXLC-250/ZD | 10" | 450 |  | 434 |  | 395 | 350 | 12-M20(1.0MPa) |
|  |  |  |  |  |  | 405 | 355 | 12-M24(1.6MPa) |
| LXLC-300/ZD | 12" | 500 |  | 459 |  | 445 | 400 | 12-M20(1.0MPa) |
|  |  |  |  |  |  | 460 | 410 | 12-M24(1.6MPa) |

DIMENSION   WI

| Type | Size |  | L Length |  | H Height | Connecting flange |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | φD1 Outside diameter | φD2 Bolt circle diameter | Connecting Bolts (n-M) |
|  | mm |  |  |  |  |  |  |  |
| LXXG-50/ZD | 2" | 200 |  | 253 |  | 165 | 125 | 4-M16 |
| LXXG-65/ZD | 2½" | 200 |  | 268 |  | 185 | 145 | 4-M16 |
| LXXG-80/ZD | 3" | 225 |  | 284 |  | 200 | 160 | 8-M16 |
| LXXG-100/ZD | 4" | 250 |  | 295 |  | 220 | 180 | 8-M16 |
| LXXG125/ZD | 5" | 250 |  | 310 |  | 250 | 210 | 8-M16 |
| LXXG-150/ZD | 6" | 300 |  | 339 |  | 285 | 240 | 8-M20 |
| LXXG-200/ZD | 8" | 350 |  | 382 |  | 340 | 295 | 8-M20(1.0MPa) |
|  |  |  |  |  |  |  |  | 12-M20(1.6MPa) |
| LXXG-250/ZD | 10" | 450 |  | 438 |  | 395 | 350 | 12-M20(1.0MPa) |
|  |  |  |  |  |  | 405 | 355 | 12-M24(1.6MPa) |
| LXXG-300/ZD | 12" | 500 |  | 488 |  | 445 | 400 | 12-M20(1.0MPa) |
|  |  |  |  |  |  | 460 | 410 | 12-M24(1.6MPa) |

Lead the definition

| LXLC(WI)-50～300/ZD Photoelectric Direct Reading Water meter |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Screw M5×45 For Sealing | Stainless Steel | 1 |
| 2 | Cover with lid | Assembly | 1 |
| 3 | Register | Assembly | 1 |
| 4 | Screw | Stainless Steel | 1 |
| 5 | Circlip | ABS | 4 |
| 6 | Fixed clamps | Stainless Steel | 1 |
| 7 | Circlip | ABS | 1 |
| 8 | Mechanism | Assembly | 3 |
| 9 | O-ring | Rubber | 4 |
| 10 | Body | Grey cast iron | 1 |

LIANYUNGANG HYTTEN METER CO.,LTD.

Address: NO.8 Hanguo Industrial Development Zone,Luoyang village,Dunshang Town,Ganyu District, Lianyungang City.

Tel：0518-85907891         Fax：0518-85907892

Http：//www. hyttenmeter.com  E-mail：hytten@hyttenmeter.com