LXSG-15-20MM Multi-jet Vane Wheel Dry-dial Cold(hot) water meter. Application: --Measuring the total volume of cold(hot) water passing through the pipeline. -NOTE:This type of water meter can be used for a reading transmission system as equipped with a bulit-in-sensor. Feature: --Multi-jet, dry-dial; Magnetic drive. --Vacuum sealed register ensures the dial keep free from fog and frost, Keep the reading clear in a long term service; --Removable measuring unit,easy installation and maintenance, Anti-magnetic function. --Brass body,Out-adjust,Small volume and light weight. -- Technical data conform to international standard ISO4064 Class B Working condition: Water temperature: T30 T50 T90 Water pressure class: MAP16 MAP10 Pressure-loss Class: △p63 Maximum permissible error: (1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%. (2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%; (Hot water meter ±3%) - MAIN TECHNICAL SPECIFICATIONS(R80/100) Type; Size; Class; Q4 Overload Flow; Q3 Permanent Flow; Q2 Transitional Flow; Q1 Minimum Flow; Minimum Reading; Maximum Reading. m3/h; m3. LXSG-15; ½"; R80 (R100); 3.125; 2.5; 0.05; 0.03125; 0.00005; 99,999. LXSG-20; ¾"; 5; 4; 0.08; 0.05; 0.00005; 99,999. - DIMENSIONS Type; Size; L Length; B Width; H Height; Connecting Thread. mm; d. LXSG-15m; ½"; 165; 89; 98; G3/4. LXSG-20m; ¾"; 190; 89; 98; G1.

| LXSG-15M-20M MULTI-JET, VANE WHEEL, DRY-DIAL WATER METER |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Lid | HDPE | 1 |
| 2 | Hinge Pin | Stainless | 1 |
| 3 | Cap | Brass | 1 |
| 4 | Sliding Gasket | PP | 1 |
| 5 | Glass Fixing Ring | ABS | 1 |
| 6 | Glass | Tempered Glass | 1 |
| 7 | O-ring | Silicon Rubber | 1 |
| 8 | Register Fixing Ring | ABS | 1 |
| 9 | Register | Assembly | 1 |
| 10 | Central Gear | Component | 1 |
| 11 | Magnetic Shield Ring | Iron | 1 |
| 12 | Gearing box | ABS Plastic | 1 |
| 13 | Tightening Gasket | Rubber | 1 |
| 14 | Turbine Component | Component | 1 |
| 15 | Measuring Chamber | HIPS | 1 |
| 16 | Bottom Strainer | LDPE | 1 |
| 17 | Body | Brass | 1 |
| 18 | Adjusting Screw | POM | 1 |
| 19 | Adjusting Gasket | Nylon | 1 |
| 20 | Adjusting Plug | Brass | 1 |
| 21 | Inlet Strainer | PP | 1 |
| 22 | Coupling Gasket | Rubber | 2 |
| 23 | Coupling Tail Piece | Brass | 2 |
| 24 | Coupling Nut | Brass | 2 |

LIANYUNGANG HYTTEN METER CO.,LTD.

Add:No. 8 Hanguo Industrial Development Zone,Luoyang Village

Dunshang Town,Ganyu District, Lianyungang, Jiangsu, China

Tel:      ++86-518-85907891

Fax:     ++86-518-85907890             Postal code:   222000

E-mail: hytten@hyttenmeter.com

http://www.hyttenmeter.com    www.hyttenwatermeter.com