LXSG-15～50

Multi-jet, vane wheel, dry-dial water meter

Application:

--Measuring the total volume of cold(hot) water passing through the pipeline.

Feature:

--Multi-jet, dry-dial; Magnetic drive.

--Vacuum sealed register ensures the dial keep free from fog and frost, Keep the reading clear in a long term service;

--Removable measuring unit,easy installation and maintenance, Anti-magnetic function.

--Measuring high flowtate with low head loss,inner and outside adjustment is optional;

-- Technical data conform to international standard ISO4064 Class B

Working condition:

Water temperature: T30 T50 T90

Water pressure class: MAP16  MAP10

Pressure-loss Class: △p63

Maximum permissible error:

(1) From minimum flow-rate(Q1) inclusive to transitional flow-rate(Q2) exclusive±5%.

(2) From transitional flow-rate(Q2) to overload flow-rate(Q4):±2%;

(Hot water meter ±3%)

- MAIN TECHNICAL SPECIFICATIONS(R80/100)

| Type | Size | Class | Q4 Overload Flow | Q3 Permanent Flow | Q2 Transitional Flow | Q1 Minimum Flow | Minimum Reading | Maximum Reading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | m3/h |  |  |  | m3 |  |
| LXSG-15 | ½" | R80 (R100) | 3.125 | 2.5 | 0.05 | 0.03125 | 0.00005 | 99,999 |
| LXSG-20 | ¾" |  | 5 | 4 | 0.08 | 00.05 | 0.00005 | 99,999 |
| LXSG-25 | 1" |  | 7.875 | 6.3 | 0.126 | 0.07875 | 0.00005 | 99,999 |
| LXSG-32 | 1¼" |  | 12.5 | 10 | 0.2 | 0.125 | 0.00005 | 99,999 |
| LXSG-40 | 1½" |  | 20 | 16 | 0.32 | 0.2 | 0.00005 | 99,999 |
| LXSG-50 | 2" |  | 31.25 | 25 | 0.5 | 0.3125 | 0.00005 | 99,999 |

- DIMENSIONS

| Type | Size | L Length | B Width | H Height | Connecting Thread |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | mm |  |  |  | d | R |
| LXSG-15 | ½" | 165 | 98 | 116 | G3/4 | R1/2 |
| LXSG-20 | ¾" | 190 | 98 | 117 | G1 | R3/4 |
| LXSG-25 | 1" | 260 | 104 | 124 | G11/4 | R1 |
| LXSG-32 | 1¼" | 260 | 104 | 124 | G11/2 | R11/4 |
| LXSG-40 | 1½" | 300 | 125 | 162 | G2 | R11/2 |
| LXSG-50 | 2" | 300 | 125 | 162 | G21/2 | R2 |

| LXSG-15～50 MULTI-JET, VANE WHEEL, DRY-DIAL WATER METER |  |  |  |
| --- | --- | --- | --- |
| Code | Description | Material | QTY |
| 1 | Lid | HDPE（ABS） | 1 |
| 2 | Hinge Pin | Stainless steel | 1 |
| 3 | Cap | Brass | 1 |
| 4 | Sliding Gasket | PP | 1 |
| 5 | Transparent cover | PC | 1 |
| 6 | O-ring | Silicon Rubber | 1 |
| 7 | Register | Assembly | 1 |
| 8 | Central Gear | Component | 1 |
| 9 | Magnetic Shield Ring | Iron | 1 |
| 10 | Gearing box | ABS Plastic | 1 |
| 11 | Tightening Gasket | Rubber | 1 |
| 12 | Turbine Component | Component | 1 |
| 13 | Measuring Chamber | HIPS | 1 |
| 14 | Bottom Strainer | LDPE | 1 |
| 15 | Gasket | Silicon Rubber | 1 |
| 16 | Body | Brass，or Iron,Plastic | 1 |
| 17 | Adjusting Screw | POM | 1 |
| 18 | Adjusting Gasket | Nylon | 1 |
| 19 | Adjusting Plug | Brass | 1 |
| 20 | Inlet Strainer | PP | 1 |
| 21 | Coupling Gasket | Rubber | 2 |
| 22 | Coupling Tail Piece | Brass | 2 |
| 23 | Coupling Nut | Brass | 2 |

LIANYUNGANG HYTTEN METER CO.,LTD.

Add:No. 8 Hanguo Industrial Development Zone,Luoyang Village

Dunshang Town,Ganyu District, Lianyungang, Jiangsu, China

Tel:      ++86-518-85907891

Fax:     ++86-518-85907892             Postal code:   222000

E-mail: hytten@hyttenmeter.com

http://www.hyttenmeter.com    www.hyttenwatermeter.com